# Building Facts Brief

2751 E Oakland Park Blvd, Fort Lauderdale, FL 33306

Prepared for: Jim Diehl, PE  ·  Project: Awa Na Kava change-of-occupancy build-out  ·  Rev. June 4, 2026

## Proposed Floor Plan

The proposed layout as drafted. Shows the restrooms, owner’s office, kitchen with the new L-shaped wall, the 14-ft caster bar (movable equipment, N.I.C.), seating arrangement, and pergola lounge. PDF copy bundled with the deployment package for full vector resolution.

## A.  Building — Confirmed

| Address / Folio | 2751 E Oakland Park Blvd, FTL FL 33306 · Folio 4942-24-03-0050. Originally filed in 1965 under 2749 E Oak Pk Blvd; bay renumbered to 2751 later. |
| --- | --- |
| Legal description | East ½ of Lot E, less the South 50 ft, Block 13, Coral Ridge Galt Addition No. 3 (PB 35, Pg 47). Lot dimensions of record: 50 × 150 ft (master permit p0022 + McLaughlin survey 4/2/1965, p0023). |
| Year built | 1965. Certificate of Occupancy #5388 issued October 19, 1965. |
| Construction type / classification | CBS — concrete block, stucco exterior. Reinforced-concrete foundation. Type II construction, Group G, Fire Zone 2 per 1965 South Florida Building Code (p0024). |
| Structure / age uniformity | 2751 and the adjoining 2747 bay built as one structure in a single 1965 event. Demising wall 8-inch CMU. Structural system and age uniform across the suite. |
| Original permits (1965) | Building FL-65-4067 · Roof FL-65-4068 · Original A/C permit #9484 (3-ton electric rooftop, Air Conditioning Associates, 7/28/1965). Architect: Richard A. Baker. Original GC: Sepper Development Co. |

## B.  Interior & Systems — Confirmed (Existing Conditions)

| Existing interior layout | Current interior partition layout is a 1982 tenant build-out (Chisholm Realty, permit #82-7116, Robert Brewster Construction). Not original 1965 fabric. |
| --- | --- |
| Original fire-rating regime (1965) | 1965 plan check (p0024) required 1-hour fire-rated interior partitions and 1-hour fire-rated ceiling throughout. |
| Drainage | 4″ cast-iron soil stack present; confirmed at three points. Note: landlord is replacing the cast-iron sanitary line on a separate permit (see C.1). |
| Existing customer restroom | Small CMU-bound room, ~52.75″ × 59.5″. Being reworked under this permit (see C.3) — NOT turn-key. |
| Abandoned storage-room plumbing | Behind the customer-restroom wall — retains drain rough-in plus copper supply routed to attic. Reuse path for the required FDACS mop / service sink (C.4). |
| Water heater | No existing WH. Attic space directly above both bathrooms is the install location; dedicated circuit already exists (see C.5). |
| Electrical — original 1965 service | 400 Amp main, dual metering, EMT wiring (p0024). Since downsized; the external “2751 A” panel (E.2) is likely a vestige of the original 400A configuration. |
| Electrical — current main panel | Frank Adam, 125A, 20 slots (16 used, 4 spare). Installed 2008 (Albert Siefert, EC0002423, permit PM-08120788). |

## C.  Permitted Scope of Work

C.1  Scope Split — Landlord vs. Awa Na Kava

| Item | Whose scope |
| --- | --- |
| Cast-iron sanitary line replacement + toilet flange set | Landlord (separate permit). Awa Na Kava relays flange position as one-line ask. |
| All other wall plumbing (lavatory, mop sink), WH install, electrical, partitions, finishes, kitchen wall | Awa Na Kava (this permit). IDB CGC1514991 as GC of record. |
| 14-ft caster bar | Awa Na Kava — movable equipment, N.I.C. (shown on plans, not as construction). See C.6. |

C.2  Kitchen — New L-Shaped Wall + Feeds

The major new construction. New L-shaped kitchen wall with the plumbing and electrical feeding into that wall. See Section H (Proposed Designs — Kitchen) for layout intent.

C.3  Customer Restroom — Maximum Extent Feasible

Existing CMU-bound room cannot meet full 60″ ADA clearance / turning space; CMU walls are a hard structural constraint. The restroom proceeds as MAXIMUM EXTENT FEASIBLE per ADA §202.3 / FBC-EB §306.6. Sealed technical-infeasibility memo accompanies the set, citing Access Board Guide to ADA Standards Ch. 2 (Feb. 2014) and DOJ Title II preamble on plumbing-wall infeasibility.

Governing codes: 2010 ADA Standards · FBC-Accessibility 2023 · FBC-Building 2023 · FBC-Plumbing 2023 · FBC-Existing Building 2023 (8th ed.) · ICC A117.1-2017.

| Water closet (toilet) | Floor-mounted, standard (NOT wall-hung). Flange centerline 17″ ± ½″ from side wall (target; code-allowed range 16″ min to 18″ max per §604.2). This is MANDATORY — landlord is fully re-running the cast-iron drain, so the prior “can’t move the toilet” constraint is removed; centerline must be brought to compliance. Set against the 59.5″ wall (rear); open/transfer side toward door — left vs. right side wall is a layout choice. Seat 17–19″ AFF. Side grab bar 42″ min (33–36″ AFF, 12″ max from rear wall, §604.5.1); rear 36″ min (§604.5.2); solid blocking during drywall. HARD CHECKPOINT: once the slab closes, flange position is locked — written rough-in dimension to landlord’s plumber before slab closure. One-line ask to landlord PM: “When the new flange is set, place centerline 17″ off the [chosen] side wall.” No wall plumbing, no added cost — lateral position on a drain being re-laid anyway. |
| --- | --- |
| Lavatory (Awa Na Kava plumber) | Wall-mount corner sink, min footprint, tucked into corner. Sits OUTSIDE the WC clear floor space (§606.2); may overlap turning space + own approach. Rim ≤ 34″ AFF (§606.3); knee 27″h × 8″ deep (§306.3); toe 9″h (§306.2). Lever or touchless (§309.4). §606.5 pipe protection: supply + drain + P-trap insulated (foam wraps, Truebro/Lav-Guard). Rough-in (Awa Na Kava plumber, stub from wall at corner): drain branch + vent stubbed at corner; hot/cold supply stub-outs at corner — CONFIRM WALL vs. FLOOR ROUTING WITH PLUMBER (do not assume); heights so finished rim ≤ 34″; pipe insulation per §606.5. |
| Door | Existing 24″ widened to 32″ in the ~36″ wall-to-wall hallway (34″ rough opening + casing fits). Nets ~30″ clear — documented as MAX-EXTENT-FEASIBLE (widening further would require relocating EP-panel wall + electrical — disproportionate / not pursued). Door swings OUTWARD (or sliding) — eliminates in-swing maneuvering-clearance conflict (§603.2.3). Annotate “max extent feasible” on the plan. |
| Clear floor space | WC: 56″ deep provided (have 59.5″) + max achievable open-side width (~35.75″). Open-side shortfall vs. 60″ documented as max-extent-feasible departure. Lav approach may overlap WC clearance + turning space (§606.2 allows). |
| Restroom count | One single-user accessible unisex restroom. FBC-Plumbing 2023 permits a single-user room “available to all persons regardless of sex” to count toward required fixtures (Group B / <50). Constrained 52.75″ × 59.5″ room does NOT auto-force a second restroom at this occupant load; Jim confirms against the occupant-load calc. |
| Verify on the drawn geometry (Jim) | • Corner lavatory + its 30″ × 48″ approach must NOT push the WC off the 17″ centerline. • Supply-line routing for the lavatory is a plumber-scope confirmation (wall vs. floor) — get the yes before travel. • Door swing must clear maneuvering space inside the room. |

C.4  Mop / Service Sink — Reuse Storage-Room Plumbing

REQUIRED — the §422.7 occupant-load ≤ 15 service-sink exemption is Business/Mercantile only, and a beverage use plans on needing it. Show on drawings reusing the abandoned storage-room plumbing behind the customer-restroom wall.

C.5  Water Heater — New Install in Attic

No existing WH. Install in attic space directly above both bathrooms. Dedicated circuit already exists (Nick will supply circuit details — see top note).

C.6  Caster Bar — Movable Equipment (N.I.C.)

NOTE — correct any prior “built-in bar” assumption: the bar is NOT fixed construction. It is movable equipment.

14-ft single solid top on lockable rolling casters. NOT a fixed/built partition. Show on drawings as movable equipment / N.I.C., not as construction. To hold that classification: not anchored to floor or walls; carries NO plumbing and NO hardwired electrical (cord-and-plug only); positioned so it does not block required egress width or accessible route.

Strings that still attach despite “movable”:

• ADA §904.4 accessible service counter segment wherever customers pay: ≥ 36″ long at ≤ 36″ high (parallel; 30″ × 48″ CFS) OR ≥ 30″ long with knee clearance (forward). Build into one bar module.

• FDACS: food/drink contact surfaces smooth, nonabsorbent, cleanable (NSF-style); sealed top, no raw-wood contact surface.

C.7  Engineering Notes to Carry on the Drawings

Synthesis of items that must appear on the stamped set:

• Floor-mounted WC at 17″ CL (landlord scope) with side & rear grab bars + solid blocking

• Wall-mount corner lavatory with §606.5-protected stubs (Awa Na Kava scope)

• Mop / service sink reusing the abandoned storage-room plumbing

• Water heater in attic above bathrooms (existing dedicated circuit)

• 32″ outward-swing restroom door (annotated “max extent feasible”)

• Caster bar shown as movable equipment / N.I.C. with §904.4 accessible service segment built into one bar module

• Restroom MAXIMUM EXTENT FEASIBLE per ADA §202.3 / FBC-EB §306.6 — sealed technical-infeasibility memo accompanies (Access Board Guide to ADA Standards Ch. 2 (Feb. 2014) + DOJ Title II preamble on plumbing-wall infeasibility)

• WC centerline brought to §604.2 compliance (drain fully re-run by landlord)

C.8  Expected Stamped Set Components

For alignment of expectations — the stamped set is anticipated to include:

• Cover / code-summary sheet — occupancy class (target Group B, <50 occ), occupant load, code editions

• Life-safety / egress plan

• Architectural floor plan — partition layout, finishes

• ADA / accessibility plan + details — restroom (MEF), 32″ outward door, §904.4 service counter, accessible route

• Plumbing plan — restroom, lavatory, mop sink, water heater

• Electrical plan — panel/circuits (incorporating Freddie’s sketch), new loads, lighting

• Mechanical — AC (pending nameplate) + ventilation

• Engineer’s calcs — Florida Energy Code forms (change of occupancy), occupant-load calc, sealed technical-infeasibility memo (restroom)

• Caster bar shown as movable equipment, N.I.C.

## D.  Change-of-Occupancy Design Items (General)

Proposed use: botanical / kava beverage lounge. No alcohol. No commercial cooking — plug-in appliances only. The following govern:

- Occupant load & group: ~38 at 15 SF/person — Group B, <50 threshold (IBC §303.1.2). Holding under 50 keeps fixture ratios gentle and supports the single-restroom count. Crossing to 50+ flips occupancy to Group A-2 (assembly): heavier fixture ratios, public restrooms must satisfy the 3:2 women’s water-closet requirement. Tune seating to maintain.

- Life safety: at this load/occupancy, assessed as not requiring sprinklers or a fire-alarm system, single exit acceptable (FBC 2023 + NFPA 101). For your confirmation.

- FDACS sinks — three required: dedicated handwash, 3-compartment, mop/utility (C.4).

- Energy calculations: required for the change of occupancy (FBC Energy Code, C503).

- ADA / accessibility: inspection is separate from final — accessibility designed in from the start. Restroom carries a sealed technical-infeasibility memo.

- DBPR — not triggered for this scope. Phase 1 beverage / prepackaged is statutorily excluded under Fla. Stat. §509.013(5)(b)(6). (Air fryer is a later-phase concern, deferred.)

## E.  To Be Field-Verified Before Drawings Finalize

These two items are not yet confirmed and should be resolved on-site before drawings are locked:

| 1 | Unidentified floor pipe (“CI-06”). Confirmed NOT a gas line; most likely an abandoned domestic-supply or condensate line, identity unconfirmed. Pressure test required before the wall is closed. |
| --- | --- |
| 2 | Second / external electrical panel (labeled “2751 A,” ~80A). Capacity and active-vs-abandoned status unconfirmed. Likely a remnant of the original 400A service split. Blocks finalization of the electrical drawings; needs an electrician walkthrough. |

Primary-source references: Seven 1965 microfilm pages (p0020 cross-sections, p0021 plot plan + elevations, p0022 master permit FL-65-4067, p0023 McLaughlin survey, p0024 plan check, p0025 floor plan, p0033 A/C permit #9484) are embedded in the web version of this brief as the source of record. The web version also includes 40 proposed-design renderings grouped by area (Kitchen, Customer Restroom, Employee Restroom, Bar Lounge, Pergola Lounge, Office).

Source note: Building identity, vintage, permit, and structural facts from the 1965 City of Fort Lauderdale microfilm. Existing-condition facts from direct site observation. Restroom configuration documented as maximum extent feasible per ADA §202.3 / FBC-EB §306.6; sealed technical-infeasibility memo accompanies the permit set. Calculated items (occupant load, life-safety thresholds) are engineering estimates for your confirmation, not authority determinations.